SimpleSox Specification:

Old Format / Location:  		Division 15, Section 15800

2005 MasterSpec Format: 	Section/Category:  [23 37 16]

PART 1-GENERAL (Division 15, Section 15800)

1.01	DESCRIPTION OF WORK:

A.	Extent of non-metal ductwork is indicated on drawings and by requirements of this section.

B.	Types of non-metal ductwork required for this project include the following:

1.	Fabric Air Dispersion Products.

1.02	QUALITY ASSURANCE:

A.	Building Codes and Standards:

1.	Product must be Classified by Underwriter’s Laboratories in accordance with the 25/50 flame spread / smoke developed requirements of NFPA 90-A and are also classified in accordance with ICC Evaluation Service AC167 and UL 2518.

2.	All product sections must be labeled with the logo and classification marking of Underwriter’s Laboratories.

B.	Design & Quality Control

1.	Manufacturer must have documented design support information including duct sizing, vent and orifice location, vent and orifice sizing, length, and suspension.  Parameters for design, including maximum air temperature, velocity, pressure and fabric permeability, shall be considered and documented.

1.03	SUBMITTALS:

A.	Product Data: Submit manufacturer’s specifications on materials and manufactured products used for work of this section.

B.	Building Code Data: Submit UL file number under which product is Classified by Underwriter’s Laboratories UL 2518.

1.04	WARRANTY

A.	Manufacturer must provide a 1 Year Product Warranty for products supplied for the fabric portion of this system as well as a Design and Performance Warranty.

1.05	DELIVERY, STORAGE AND HANDLING:

A.	Protect fabric air dispersion systems from damage during shipping, storage and handling.

B.	Where possible, store products inside and protect from weather.  Where necessary to store outside, store above grade and enclose with a vented waterproof wrapping.

PART 2 - PRODUCTS

2.01	MANUFACTURER:

Subject to compliance with requirements, choose one of the following:

A.	DuctSox® Corporation

Phone: 		(866) DUCTSOX 	or  	(563) 588-5300

FAX:     	(866) 398-1646 		or  	(563) 588-5330

www.DuctSox.com

2.02	FABRIC AIR DISPERSION SYSTEM:

A.	SimpleSox Fabric: Air diffusers shall be constructed of a coated woven fire retardant fabric complying with the following physical characteristics:

1.	Fabric Construction: 100% Polyester

2.	Coating: Non-air permeable coating

3.	Weight: 5.5 oz./yd2 per ASTM D3776

4.	Color: White or Silver

5.	Air Permeability: 0 cfm/ft2 per ASTM D737, Frazier

6.	Temperature Range: 0 degrees F to 180 degrees F

7.	Fire Retardancy: Classified by Underwriters Laboratories in accordance with the flame spread/smoke developed requirements of NFPA 90-A and UL 2518.

B.	SYSTEMS FABRICATION REQUIREMENTS:

1.	Dispersion design completed by Adjustable Air Outlet

2.	Inlet connection to metal duct via fabric draw band with anchor patches as supplied by manufacturer.  Anchor patches to be secured to metal duct via. zip screw fastener – supplied by contractor.

3.	Modular Lengths to include required zippers as specified by manufacturer.

5.	System to include Adjustable Flow Devices to balance turbulence, airflow and distribution as needed.  Flow restriction device shall include ability to adjust the airflow resistance from 0.06 – 0.60 in w.g. static pressure.

6.	Fabric system shall include connectors to accommodate suspension system listed below.

7.	Any deviation from a straight run shall be made using a gored elbow or an efficiency tee.  Normal 90 degree elbows are 5 gores and the radius of the elbow is 1.5 times the diameter of the DuctSox.

C.	DESIGN PARAMETERS:

1.	Fabric air diffusers shall be designed with 0.5” as the standard.

2.	Fabric air diffusers shall be limited to design temperatures between 0 degrees F and 180 degrees F (-17.8 degrees C and 82 degrees C).

3.	Design CFM, static pressure and diffuser length shall be designed or approved by the manufacturer.

4.	Do not use fabric diffusers in concealed locations.

5.	Use fabric diffusers only for positive pressure air distribution components of the mechanical ventilation system.

D.	SUSPENSION HARDWARE:

Tension Cable:  System shall be installed using a tension cable system including a single (1 Row) of cable located 1.5” above top-dead-center.  Hardware to include cable, eye bolts, thimbles, cable clamps and turnbuckle(s) as required. System attachment shall be made using nylon cable clips.

***END OF SECTION***

PART 3 - INSTALLATION

3.01	INSTALLATION OF FABRIC AIR DISPERSION SYSTEM:

A.	Install chosen suspension system in accordance with the requirements of the manufacturer.  Instructions for installation shall be provided by the manufacturer with product.

3.02	CLEANING AND PROTECTION:

A.	Clean air handling unit and ductwork prior to the DuctSox system unit-by-unit as it is installed.  Clean external surfaces of foreign substance which may cause corrosive deterioration of facing.

B.	Temporary Closure: At ends of ducts which are not connected to equipment or distribution devices at time of ductwork installation, cover with polyethylene film or other covering which will keep the system clean until installation is completed.

C.	If DuctSox systems become soiled during installation, they should be removed and cleaned following the manufacturers standard terms of laundry.

***END OF SECTION***